## Form Blueprint
Universal Commercial HVAC PM Form - Recommended Structure
Step | Form Section | Record Level | Contents | Design Notes
1 | Customer Profile / Rules | Hidden configuration selected by customer or call center | Required setpoints, seasonal scope, photo rules, timestamp requirement, anti-algae requirement, signature/site stamp, submission deadline, IVR instructions, NTE/quote rules | Prevents conflicting customer rules from being hard-coded into one universal form.
2 | Site Visit Header | One record per work order/site visit | Customer, call center, work order, IVR, site, address, service date, technician, manager, access, PM season, unit count, arrival/departure | Complete before the first unit.
3 | Unit Equipment Record | Repeat once for every piece of HVAC equipment | Unit ID, equipment type, location, area served, manufacturer, model, serial, age, tonnage, heat type, refrigerant, filters, belts, asset condition | A separate unit record is required even when multiple units are on one work order.
4 | Core PM Checklist | Shown for every unit | Cabinet, filters, coils, fans, belts, drains, electrical, controls, thermostat, operation, cleanup | Use standardized results: Pass / Needs Service / Failed-Replace / N/A / Not Accessible.
5 | Cooling / Refrigeration Section | Conditional | Pressures, temperatures, superheat, subcooling, charge, leaks, compressors, condenser fans, line insulation, reversing valve | Show when cooling, heat-pump, refrigeration, VRF, or water-source equipment applies.
6 | Heating Section | Conditional | Gas/electric/hydronic heating, gas pressure, burners, ignition, heat exchanger, flue, safety switches, temperature rise | Show only the applicable heat type.
7 | Hydronic / Water-Cooled Section | Conditional | Entering/leaving water temperatures, regulating valve, strainers, flow/pressure drop, glycol, freeze protection | Show for water-source, chilled-water, hot-water, or water-cooled equipment.
8 | Controls / EMS / Economizer Section | Conditional | Thermostat, remote sensors, programming, schedules, setpoints before/after, DDC/BAS, dampers, economizer, alarms | Customer-required setpoints come from the customer profile.
9 | Photos | One site package plus repeated unit photo package | Building front, unit location, nameplate, exterior, filters, interior, coils, drains, belts, electrical, thermostat, deficiencies, readings, cleanup | The form should force photos only when required by customer rules or when a deficiency is found.
10 | Deficiency / Quote Record | Repeat for each issue found | Unit, component, condition, severity, impact, recommended action, parts, estimated labor, NTE/quote, call-center notification, photos | Keeps recommendations specific and quote-ready.
11 | Materials Used | Repeat as needed | Filters, belts, refrigerant, batteries, anti-algae tablets, fuses, contactors, miscellaneous materials; size/type/quantity | Supports invoice validation and replenishment.
12 | Closeout / Signoff | One record per visit | Full scope completed, unit left operating, manager informed, manager name/signature, technician signature, IVR checkout, documents/photos attached, submission date | If work is incomplete, require the reason and call-center notification details.
Key Design Decision
Build one dynamic form, not one giant static checklist. Select the customer profile, PM season and equipment type first. The form should then display the required tasks, readings, customer-specific setpoints and photos. This resolves conflicts such as Off Broadway requiring 70°F cooling while Rack Room requires 71°F.
Workbook Summary | Count
Master data fields | 216
PM tasks / inspections | 86
Photo requirements | 28
Customer-specific exception rules | 20

## Master Data Fields
Definitive Master Data Dictionary
cl_name | Field ID | Section | Subsection | Field / Question | Input Type | Allowed Values / Format | Requirement | Trigger / Applies When | Source Coverage | Photo Needed for this step? | Man hors per task | Daniel/Implementation Notes
HVAC PM Checklist | F001 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Customer / Client | Dropdown | Configured customer list | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation.
HVAC PM Checklist | F002 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Call center / facility management provider | Dropdown/Text | Configured provider list | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F003 | 3 - Ticket Entry | Work Order & Arrival | Work order number | Text | Customer WO / vendor WO | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS / Under Armour, Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F004 | 3 - Ticket Entry | Work Order & Arrival | IVR PIN / check-in number | Text | Digits/text | Conditional | Customer uses IVR | BOSS Facility Services, Laser Facility / Kelly Services | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F005 | 3 - Ticket Entry | Work Order & Arrival | IVR check-in time / confirmation | Date-Time/Text | Timestamp and confirmation number | Conditional | Customer uses IVR | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F006 | 3 - Ticket Entry | Work Order & Arrival | IVR checkout / closeout number | Text | Digits/text | Conditional | Customer uses IVR | Powerhouse / Hibbett Sports, Laser Facility / Kelly Services | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F007 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Location / store number | Text | Customer location ID | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F008 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Site / store name | Text | Free text | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F009 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Shopping center / mall | Text | Free text | Conditional | Retail location or customer requests | Victoria's Secret & Co. | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F010 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Street address | Text | Free text | Always | Every visit | BOSS Facility Services, First Cash | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F011 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | City | Text | Free text | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F012 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | State | Dropdown/Text | 2-letter state | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F013 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | ZIP code | Text | 5 or 9 digits | Always | Every visit | First Cash | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F014 | 3 - Ticket Entry | Work Order & Arrival | Service date | Date | MM/DD/YYYY | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F015 | 3 - Ticket Entry | Work Order & Arrival | Arrival time | Time | HH:MM | Recommended | Every visit | Industry best-practice addition | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F016 | 1 - Already Built Into EvoTrakker | Work Order & Arrival | Departure time | Time | HH:MM | Recommended | Every visit | Industry best-practice addition | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F017 | 3 - Ticket Entry | Work Order & Arrival | PM season / visit type | Dropdown | Spring Cooling; Fall Heating; Full PM; Inspection Only; Filter Change; Other | Always | Every visit | Victoria's Secret & Co., CLS / Under Armour | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F018 | 3 - Ticket Entry | Work Order & Arrival | Technician name | Text/Dropdown | Employee list | Always | Every visit | Victoria's Secret & Co., First Cash | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F019 | 3 - Ticket Entry | Work Order & Arrival | Technician employee ID | Text | Employee number | Recommended | Every visit | Industry best-practice addition | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F020 | 3 - Ticket Entry | Work Order & Arrival | Submitted by | Text | Name | Conditional | Separate submitter required | First Cash | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F021 | 3 - Ticket Entry | Work Order & Arrival | Submitter phone | Phone | Phone number | Conditional | Separate submitter required | First Cash | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F022 | 3 - Ticket Entry | Work Order & Arrival | Submitter email | Email | Email address | Conditional | Separate submitter required | First Cash | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F023 | 4 - Tech Entry Check In | Work Order & Arrival | Site manager / contact name at arrival | Text | Free text | Always | Occupied site | Laser Facility / Kelly Services | N | 0.016667
HVAC PM Checklist | F024 | 4 - Tech Entry Check In | Work Order & Arrival | Manager notified of arrival | Yes/No | Yes; No; N/A | Always | Occupied site | Laser Facility / Kelly Services | N | 0.016667
HVAC PM Checklist | F025 | 3 - Ticket Entry | Work Order & Arrival | Special access requirements | Multi-select/Text | Roof hatch; Ladder; Lift; Key; Locked area; Escort; Ceiling access; Other | Always | Every visit | Laser Facility / Kelly Services | N | 0.016667 | Modify ticket creation!!! Have a drop down list from which to choose… if customer does not provide, needs to be verified each time to ensure tech arrives with correct equipment/instructions!!!
HVAC PM Checklist | F026 | 3 - Ticket Entry | Work Order & Arrival | Unit location description | Dropdown | Ground, Rooftop, Stilts, Fenced area on the ground, fenced area on the roof | Always | Each unit | Laser Facility / Kelly Services | Y | 0.016667 | Modify ticket creation!!! Ask customer for general location of each unit.
HVAC PM Checklist | F0TBD | 4 - Tech Entry Check In | Work Order & Arrival | Access / safety issues found | Multi-select/Text | Unsafe roof; No ladder; Locked; Weather; Electrical hazard; Animal/pest; Other | Conditional | Any access problem | Industry best-practice addition | Y | 0.016667 | Move to Service Checklist items near reason could not do the service
HVAC PM Checklist | F028 | 3 - Ticket Entry | Work Order & Arrival | Number of units expected | Dropdown | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, More than 25 (maybe require additional?) | Recommended | Every visit | Industry best-practice addition | N | 0.016667 | Modify ticket creation!!! Ask customer for number of units. If unknown, add this as an option. What is selcted here will expand/contract the EvoTrakker PM Checklist. Have option so that tech can expand/contract that list but it would start out with the number chosen here.
HVAC PM Checklist | F029 | 7 - Tech Entry Check Out | Work Order & Arrival | Number of units serviced | Dropdown | 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, More than 25 (maybe require additional?) | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | Modify ticket creation!!! Ask customer for number of units. If unknown, add this as an option. What is selcted here will expand/contract the EvoTrakker PM Checklist. Have option so that tech can expand/contract that list but it would start out with the number chosen here.
HVAC PM Checklist | F030 | 7 - Tech Entry Check Out | Work Order & Arrival | Full contracted scope completed | Yes/No | Yes; No | Always | Every visit | CLS Equipment Condition Report, CLS / Under Armour | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F031 | 7 - Tech Entry Check Out | Work Order & Arrival | Reason full scope not completed | Long text | Free text | Conditional | Full scope = No | CLS Equipment Condition Report, CLS / Under Armour | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F032 | 7 - Tech Entry Check Out | Work Order & Arrival | Call center notified about incomplete work | Yes/No | Yes; No; N/A | Conditional | Full scope = No | CLS Equipment Condition Report, CLS / Under Armour | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F033 | 7 - Tech Entry Check Out | Work Order & Arrival | Notification contact / date / time / confirmation | Text | Name, date, time, reference number | Conditional | Call center notified | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F034 | 2 - PM Rules by Parent Trade | Work Order & Arrival | Required cooling setpoint | Dropdown | 68°F, 69°F, 70°F, 71°F, 72°F, 73°F, 74°F, 75°F, 76°F, 77°F, 78°F | Configured | Customer-specific | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F035 | 2 - PM Rules by Parent Trade | Work Order & Arrival | Required heating setpoint | Dropdown | 65°F, 66°F, 67°F, 68°F, 69°F, 70°F, 71°F, 72°F | Configured | Customer-specific | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F036 | 2 - PM Rules by Parent Trade | Work Order & Arrival | Required thermostat schedule | Dropdown | 24/7; Occupied schedule; Customer-specific | Configured | Customer-specific | Off Broadway Shoe Warehouse, Rack Room Shoes | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F037 | 2 - PM Rules by Parent Trade | Work Order & Arrival | Thermostat lock required | Yes/No | Yes, No | Configured | Customer-specific | Off Broadway Shoe Warehouse, Rack Room Shoes | N | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F038 | 2 - PM Rules by Parent Trade | Work Order & Arrival | Anti-algae treatment required | Yes/No | Yes; No | Configured | Customer-specific | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | No tech info needed - would be from ticket creation
HVAC PM Checklist | F039 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Photos must be time/date stamped | Yes/No | Yes; No | Configured | Customer-specific | Off Broadway Shoe Warehouse, Rack Room Shoes | N | 0.016667 | Already built into system… maybe name auto name photos with date and time built in?
HVAC PM Checklist | F040 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Manager must see old filters | Yes/No | Yes; No | Configured | Customer-specific | Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F041 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Pricing may be discussed with site staff | Yes/No | Yes; No | Configured | Customer-specific | Laser Facility / Kelly Services | N | 0.016667 | Laser says detailed findings/pricing should not be given to store personnel.
HVAC PM Checklist | F042 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Immediate quote required for deficiencies | Yes/No | Yes; No | Configured | Customer-specific | CLS Equipment Condition Report, CLS / Under Armour, Off Broadway Shoe Warehouse, Rack Room Shoes | N | 0.016667 | Service Checklist items… maybe create new workflow off of this
HVAC PM Checklist | F043 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Immediate call required if scope cannot be completed | Yes/No | Yes; No | Configured | Customer-specific | CLS Equipment Condition Report, CLS / Under Armour | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F044 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Submission deadline | Text/Number | Same day; within 1 week; customer-specific | Configured | Customer-specific | Broadway National / Primark | N | 0.016667 | Assume this relates to quote… move into that workflow
HVAC PM Checklist | F045 | 2 - PM Rules by Parent Trade | Customer-Specific Rules | Required closeout documents | Multi-select | Invoice; Signoff; Checklist; Photos; Quote; Site stamp | Configured | Customer-specific | Laser Facility / Kelly Services, Broadway National / Primark, BOSS Facility Services | N | 0.016667 | Check-out Checklist items
HVAC PM Checklist | F046 | 5 - Tech Entry Asset Basics | Identification & Condition | Unit number / ID | Text | Customer unit number | Always | Each unit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | y | 0.016667 | Service Checklist items
HVAC PM Checklist | F047 | 5 - Tech Entry Asset Basics | Identification & Condition | Asset tag / Tag ID | Text | Asset identifier | Conditional | Asset-tagged equipment | Powerhouse / Hibbett Sports, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F048 | 5 - Tech Entry Asset Basics | Identification & Condition | Connected equipment tag / AHU number | Text | Related asset ID | Conditional | Split systems or connected assets | Powerhouse / Hibbett Sports, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F049 | 5 - Tech Entry Asset Basics | Identification & Condition | Equipment type | Dropdown | RTU; Split System; AHU; Heat Pump; Water-Source Heat Pump; VAV; FPVAV; Fan Coil; VRF; Exhaust Fan; Refrigeration; Chiller; Boiler; Other | Always | Each unit | Broadway National / Primark, Laser Facility / Kelly Services, Victoria's Secret & Co., CLS Equipment Condition Report | N | 0.016667 | Service Checklist items - THIS LIST NEEDS TO BE UPDATED TO BETTER MATCH F051 lists… need advanced skip logic built into this version
HVAC PM Checklist | F050 | 5 - Tech Entry Asset Basics | Identification & Condition | Asset type / description | Text | Free text | Recommended | Each unit | Powerhouse / Hibbett Sports | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F051 | 5 - Tech Entry Asset Basics | Identification & Condition | Manufacturer / brand (Packaged rooftop, commercial split and broad-line manufacturers) | Dropdown | AAON; Allied Commercial; Amana; American Standard; Arcoaire; Bard; Bosch; Bryant; Carrier; Champion; Coleman; Comfortmaker; Daikin; Day & Night; Fraser-Johnston; Friedrich; Goodman; Heil; International Comfort Products/ICP; Johnson Controls; KeepRite; Lennox; Luxaire; Magic-Pak; Marvair; McQuay; Modine; NORDYNE/Nortek Global HVAC; Payne; Reznor; Rheem; Ruud; TempMaster; Tempstar; Trane; York, Other (allow box for other) | Always | Each unit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Generate master list (use AI) and have entry for other. Service Checklist items.
HVAC PM Checklist | F051-1 | 5 - Tech Entry Asset Basics | Identification & Condition | Manufacturer / brand (IF VRF or VRV) | Dropdown | Carrier; Carrier/Toshiba; CIAT; Clivet; Daikin/VRV; Fujitsu General; GENERAL; AIRSTAGE; Gree; Haier; Hitachi; Johnson Controls-Hitachi; LG; Lennox Powered by Samsung/Varix; Midea; MDV; Mitsubishi Electric; Mitsubishi Heavy Industries; Panasonic; Samsung; Sanyo; Toshiba; Trane/Mitsubishi Electric; York/Hitachi | Always | Each unit | Daniel added | Y | 0.016667 | Generate master list (use AI) and have entry for other. Service Checklist items.
HVAC PM Checklist | F051-2 | 5 - Tech Entry Asset Basics | Identification & Condition | Manufacturer / brand (IF Chiller) | Dropdown | Aermec; Airedale by Modine; Arctic Chiller Group; Broad; Carrier; CIAT; Climaveneta; Clivet; Daikin Applied; Dunham-Bush; Gree; Hitachi; Johnson Controls; LG; McQuay; Midea; Mitsubishi Electric Hydronics & IT Cooling Systems/MEHITS; Mitsubishi Heavy Industries; Motivair; Multistack; Petra; Samsung; SKM; Smardt; Swegon/Blue Box; Thermax; Thermal Care; TICA; Trane; Voltas; Yazaki; York; Zamil | Always | Each unit | Daniel added | Y | 0.016667 | Generate master list (use AI) and have entry for other. Service Checklist items.
HVAC PM Checklist | F051-3 | 5 - Tech Entry Asset Basics | Identification & Condition | Manufacturer / brand (IF Custom) | Dropdown | AAON; Addison; Air Enterprises; Alliance Air Products; Annexair; Bousquet; CaptiveAire; CleanPak; Climate by Design International; ClimateCraft; Desert Aire; Engineered Air; Energy Labs; FläktGroup; Governair; Greenheck; Haakon; Huntair; I.C.E. Western; Innovent; Johnson Air-Rotation; Mammoth; Munters; Nortek Air Solutions; Price Industries; Seasons-4; SEMCO; Swegon; Systemair; Temtrol; TICA; TROX; United CoolAir; Unison Comfort Technologies; Valent; Venmar CES; Ventrol | Always | Each unit | Daniel added | Y | 0.016667 | Generate master list (use AI) and have entry for other. Service Checklist items.
HVAC PM Checklist | F051-4 | 5 - Tech Entry Asset Basics | Identification & Condition | Manufacturer / brand (IF PTAC) | Dropdown | Amana PTAC; Applied Comfort; Bosch; Carrier; ClimateMaster; Cold Point; Daikin; Eubank; FHP; Friedrich; GE Appliances/Zoneline; Gree; Ice Air; International Environmental Corporation/IEC; Islandaire; LG; Magic-Pak; Marvair; McQuay/Enfinity; Midea; Suburban/Dynaline; Temspec; Trane; WaterFurnace; Whalen | Always | Each unit | Daniel added | Y | 0.016667 | Generate master list (use AI) and have entry for other. Service Checklist items.
HVAC PM Checklist | F052 | 5 - Tech Entry Asset Basics | Identification & Condition | Model number | Text | Free text | Always | Each unit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F053 | 5 - Tech Entry Asset Basics | Identification & Condition | Serial number | Text | Free text | Always | Each unit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F054 | 5 - Tech Entry Asset Basics | Identification & Condition | Manufactured date / year | Date/Number | YYYY or date | Recommended | Each unit | BOSS Facility Services, Powerhouse / Hibbett Sports | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F055 | 5 - Tech Entry Asset Basics | Identification & Condition | Install date | Date | MM/DD/YYYY | Conditional | Known / customer requests | Powerhouse / Hibbett Sports | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F056 | 5 - Tech Entry Asset Basics | Identification & Condition | Unit age | Number | Years | Recommended | Each unit | Broadway National / Primark, Laser Facility / Kelly Services, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F057 | 5 - Tech Entry Asset Basics | Identification & Condition | Tonnage / nominal capacity | Number/Text | Tons or BTU/h | Always | Cooling equipment | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | Service Checklist items… if possible, have this auto calculated (using AI) off model number
HVAC PM Checklist | F058 | 5 - Tech Entry Asset Basics | Identification & Condition | Rated efficiency | Text/Number | EER; SEER; IEER; COP; AFUE | Optional | Nameplate or known | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F059 | 5 - Tech Entry Asset Basics | Identification & Condition | Heating energy source | Dropdown | Gas; Electric; Heat Pump; Hot Water; Steam; Oil; None; Other | Always | Each unit | First Cash, Rack Room Shoes | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F060 | 5 - Tech Entry Asset Basics | Identification & Condition | Refrigerant type | Dropdown/Text | R-22; R-410A; R-407C; R-134a; R-32; R-454B; Other; Unknown | Always | Refrigeration equipment | CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F061 | 5 - Tech Entry Asset Basics | Identification & Condition | Area served | Dropdown | Interior Occupied Areas (inc. Salesfloor), Restrooms, Mechanical/Electrical Rooms,Common Areas (Hallways/Lobbies), Service/Back-of-House Areas (inc. Office), Multiple Interior Areas, Roof Areas, Exterior Grounds/Perimeter, Parking Areas (Garage/Lot) | Always | Each unit | BOSS Facility Services, Broadway National / Primark, Victoria's Secret & Co. | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F062 | 5 - Tech Entry Asset Basics | Identification & Condition | Shared unit | Dropdown | Yes; No; Unknown | Conditional | Tenant/shared systems | Laser Facility / Kelly Services | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F063 | 5 - Tech Entry Asset Basics | Identification & Condition | Air / water supplied by | Dropdown | Customer; Mall; Landlord; VSS; Other | Conditional | Mall/tenant systems | Victoria's Secret & Co. | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F064 | 5 - Tech Entry Asset Basics | Identification & Condition | Curb adapter present | Yes/No | Yes; No; Unknown | Conditional | RTU / customer requests | First Cash | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F065 | 5 - Tech Entry Asset Basics | Identification & Condition | Warranty period / status | Text | Years / expiration / unknown | Optional | Known | Powerhouse / Hibbett Sports | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F066 | 5 - Tech Entry Asset Basics | Identification & Condition | Unit life expectancy | Number | Estimated remaining years | Recommended | Condition survey | Powerhouse / Hibbett Sports, Vixxo / PepsiCo | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F067 | 6 - Tech Entry Unit Specifics | Identification & Condition | Overall unit condition | Dropdown | Excellent; Good; Fair; Poor; Needs Replacement | Always | Each unit | BOSS Facility Services, CLS Equipment Condition Report, Powerhouse / Hibbett Sports, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F068 | 6 - Tech Entry Unit Specifics | Identification & Condition | Overall recommendation | Dropdown | None; Monitor; Repair; Replace | Always | Each unit | CLS Equipment Condition Report, Vixxo / PepsiCo | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F069 | 6 - Tech Entry Unit Specifics | Identification & Condition | Unit operational at arrival | Dropdown | Yes; No; Partially; Unknown | Recommended | Each unit | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F070 | 6 - Tech Entry Unit Specifics | Identification & Condition | Unit operational at departure | Dropdown | Yes; No; Partially; Shut down for safety | Always | Each unit | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F071 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Filter size 1 | Dimensions | L x W x D | Always | Filtered equipment | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items - move so that each unit gets into these questions. If 1 unit - only presented one time. If 10, these would be presented 10 times
HVAC PM Checklist | F072 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Filter quantity 1 | Number | Whole number | Always | Filtered equipment | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F073 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Filter size 2 | Dimensions | L x W x D | Conditional | Multiple filter sizes | BOSS Facility Services, CLS Equipment Condition Report | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F074 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Filter quantity 2 | Number | Whole number | Conditional | Multiple filter sizes | BOSS Facility Services, CLS Equipment Condition Report | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F075 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Filter type / MERV | Text/Dropdown | Pleated; Panel; Bag; HEPA; Washable; Other; MERV rating | Recommended | Filtered equipment | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F076 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Filters replaced today | Yes/No/NA | Yes; No; N/A | Always | Filtered equipment | BOSS Facility Services, Broadway National / Primark, CLS / Under Armour, Laser Facility / Kelly Services, Powerhouse / Hibbett Sports, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F077 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Number of filters replaced | Number | Whole number | Conditional | Filters replaced | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F078 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Filters dated | Yes/No/NA | Yes; No; N/A | Conditional | Filters replaced | CLS / Under Armour, Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F079 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Filter condition before replacement | Dropdown | Clean; Lightly dirty; Dirty; Severely loaded; Damaged; Missing | Recommended | Filtered equipment | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F080 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Correct filter fit and airflow direction | Yes/No/NA | Yes; No; N/A | Recommended | Filtered equipment | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F081 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Old filters shown to store staff | Yes/No/NA | Yes; No; N/A | Conditional | Customer rule requires | Rack Room Shoes | Y | 0.016667 | Service Checklist items - this is a duplicate to F040
HVAC PM Checklist | F082 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Belt size | Text | Manufacturer size / dimensions | Conditional | Belt-driven equipment | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F083 | 5 - Tech Entry Asset Basics | Filters, Belts, Fans & Airflow | Belt quantity | Number | Whole number | Conditional | Belt-driven equipment | BOSS Facility Services, CLS Equipment Condition Report | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F084 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Belt condition | Dropdown | Good; Worn; Cracked; Glazed; Frayed; Oil-contaminated; Failed | Conditional | Belt-driven equipment | CLS / Under Armour, Powerhouse / Hibbett Sports, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F085 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Belt tension | Dropdown/Number | Good; Loose; Tight; Adjusted; Measured tension | Conditional | Belt-driven equipment | CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F086 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Belt alignment | Dropdown | Aligned; Misaligned; Corrected; N/A | Conditional | Belt-driven equipment | CLS / Under Armour | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F087 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Pulley / sheave condition | Dropdown | Good; Worn; Damaged; Loose; Replace | Conditional | Belt-driven equipment | CLS / Under Armour, Rack Room Shoes, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F088 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Pulley / shaft alignment | Yes/No/NA | Yes; No; Corrected; N/A | Conditional | Belt-driven equipment | Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F089 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Blower wheel / fan blade condition | Dropdown | Good; Dirty; Damaged; Loose; Out of balance | Always | Fan-equipped unit | BOSS Facility Services, Powerhouse / Hibbett Sports, Rack Room Shoes, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F090 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Bearing condition / lubrication | Dropdown | Good; Dry; Noisy; Loose; Lubricated; Replace | Always | Fan-equipped unit | Broadway National / Primark, Rack Room Shoes, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F091 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Blower / fan RPM | Number | RPM | Optional | Measured / customer requests | Vixxo / PepsiCo | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F092 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Supply air temperature | Number | °F | Always | Unit can run | Rack Room Shoes, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F093 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Return air temperature | Number | °F | Recommended | Unit can run | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F094 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Mixed air temperature | Number | °F | Conditional | Economizer/mixing section present | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F095 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Cooling temperature split | Formula/Number | Return minus supply °F | Always | Cooling test performed | CLS / Under Armour | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F096 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Heating temperature rise | Formula/Number | Supply minus return °F | Always | Heating test performed | CLS / Under Armour | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F097 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Entering static pressure | Number | in. w.c. | Recommended | Ducted equipment | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F098 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Leaving static pressure | Number | in. w.c. | Recommended | Ducted equipment | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F099 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Total external static pressure | Formula/Number | in. w.c. | Recommended | Static readings taken | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F100 | 6 - Tech Entry Unit Specifics | Filters, Belts, Fans & Airflow | Airflow / supply grille reading | Number/Text | CFM, velocity, or qualitative airflow | Conditional | Customer requests / complaint | Off Broadway Shoe Warehouse | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F101 | 4 - Tech Entry Check In | Filters, Belts, Fans & Airflow | Indoor / store temperature | Number | °F | Recommended | Occupied site | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F102 | 4 - Tech Entry Check In | Filters, Belts, Fans & Airflow | Outdoor ambient temperature | Number | °F | Always | Performance readings taken | BOSS Facility Services, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F103 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Number of refrigeration circuits / stages | Number | Whole number | Conditional | Refrigeration equipment | BOSS Facility Services, Victoria's Secret & Co. | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F104 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Suction pressure by circuit | Repeating number | psig for each circuit | Conditional | Cooling system operating | BOSS Facility Services, Broadway National / Primark, CLS / Under Armour, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F105 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Discharge / head pressure by circuit | Repeating number | psig for each circuit | Conditional | Cooling system operating | BOSS Facility Services, Broadway National / Primark, CLS / Under Armour, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F106 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Suction line temperature by circuit | Repeating number | °F | Recommended | Pressure readings taken | Victoria's Secret & Co., Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F107 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Liquid line temperature by circuit | Repeating number | °F | Recommended | Pressure readings taken | Victoria's Secret & Co., Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F108 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Superheat by circuit | Repeating number | °F | Conditional | Applicable metering device / system operating | Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F109 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Subcooling by circuit | Repeating number | °F | Conditional | Applicable system / system operating | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F110 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant charge / level condition | Dropdown | Proper; Low; High; Unable to verify; N/A | Always | Refrigeration equipment | BOSS Facility Services, Broadway National / Primark, Rack Room Shoes, Vixxo / PepsiCo | Maybe? | 0.016667 | Service Checklist items
HVAC PM Checklist | F111 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant added | Yes/No | Yes; No | Conditional | Charge adjusted | Victoria's Secret & Co., Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F112 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant type and amount added | Text/Number | Type and pounds/ounces | Conditional | Refrigerant added | Industry best-practice addition | Maybe? | 0.016667 | Service Checklist items
HVAC PM Checklist | F113 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant / oil leak found | Yes/No | Yes; No | Always | Refrigeration equipment | Broadway National / Primark, BOSS Facility Services, Rack Room Shoes, Vixxo / PepsiCo | Maybe? | 0.016667 | Service Checklist items
HVAC PM Checklist | F114 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Leak location / detection method | Text | Visual, electronic, bubbles, oil trace, etc. | Conditional | Leak found | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F115 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Schrader valve condition / leaks | Dropdown | Good; Leaking; Tightened; Replaced; N/A | Conditional | Service ports present | Broadway National / Primark | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F116 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Schrader caps installed / tightened | Yes/No/NA | Yes; No; N/A | Conditional | Service ports present | Broadway National / Primark | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F117 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant valve packing condition | Dropdown | Good; Leaking; Adjusted; N/A | Conditional | Valve packings present | Broadway National / Primark | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F118 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | TXV / EEV operation | Dropdown | Normal; Suspect; Failed; N/A | Conditional | Applicable metering device | Broadway National / Primark, Rack Room Shoes | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F119 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Moisture indicator condition | Dropdown | Dry; Wet; Discolored; N/A | Conditional | Sight glass present | Broadway National / Primark | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F120 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Filter-drier condition | Dropdown | Good; Restricted/Suspect; Corroded; Replace; N/A | Always | Refrigeration equipment | BOSS Facility Services, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F121 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant piping condition | Dropdown | Good; Damaged; Rubbing; Unsupported; Corroded; Leaking | Always | Refrigeration equipment | Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F122 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Refrigerant line insulation condition | Dropdown | Good; Worn; Missing; Wet; Repaired; Replace | Always | Insulated lines present | Victoria's Secret & Co., Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F123 | 6 - Tech Entry Unit Specifics | Cooling & Refrigeration Readings | Compressor oil level / condition | Text/Dropdown | Normal; Low; High; Discolored; N/A | Conditional | Sight glass / applicable compressor | Rack Room Shoes, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F124 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Incoming voltage | Repeating number | L1-L2, L2-L3, L1-L3 or L-N | Recommended | Unit energized and safe to test | Broadway National / Primark, CLS / Under Armour | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F125 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Voltage imbalance | Formula/Number | Percent | Recommended | Three-phase equipment | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F126 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Compressor running amps by compressor | Repeating number | Amps | Conditional | Cooling system operating | BOSS Facility Services, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F127 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Compressor rated amps / RLA / FLA | Repeating number | Nameplate amps | Recommended | Compressor amp readings taken | Vixxo / PepsiCo | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F128 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Condenser fan motor amps | Repeating number | Amps | Conditional | Condenser fans operating | BOSS Facility Services | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F129 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Blower / evaporator fan motor amps | Repeating number | Amps | Always | Fan operating | BOSS Facility Services, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F130 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Motor rated FLA | Number | Nameplate amps | Recommended | Motor amp readings taken | Vixxo / PepsiCo | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F131 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Electric heat amps by stage | Repeating number | Amps | Conditional | Electric heat present and tested | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F132 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Capacitor rating and measured value | Repeating number | µF rated / measured | Recommended | Capacitors present and safe to test | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F133 | 5 - Tech Entry Asset Basics | Electrical, Thermostat & Controls | Thermostat brand / model | Text | Free text | Conditional | Thermostat present | Laser Facility / Kelly Services | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F134 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat room temperature | Number | °F | Recommended | Thermostat present | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F135 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat cooling setpoint before | Number | °F | Conditional | Customer setpoint rule / thermostat present | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F136 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat heating setpoint before | Number | °F | Conditional | Customer setpoint rule / thermostat present | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F137 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat schedule before | Dropdown/Text | 24/7; Occupied; Unoccupied; Unknown; Custom | Conditional | Programmable thermostat | Rack Room Shoes, Laser Facility / Kelly Services | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F138 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat calling mode during reading | Dropdown | Cooling; Heating; Fan only; Satisfied; Off | Always | Supply temperature recorded | Rack Room Shoes | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F139 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat cooling setpoint after | Number | °F | Conditional | Customer setpoint rule | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F140 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat heating setpoint after | Number | °F | Conditional | Customer setpoint rule | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F141 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat differential | Number | °F | Conditional | Customer rule requests | Laser Facility / Kelly Services | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F142 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat locked | Yes/No/NA | Yes; No; N/A | Conditional | Customer rule requires | Off Broadway Shoe Warehouse, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F143 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Thermostat batteries replaced | Yes/No/NA | Yes; No; N/A | Conditional | Battery thermostat / batteries weak | Laser Facility / Kelly Services | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F144 | 5 - Tech Entry Asset Basics | Electrical, Thermostat & Controls | Remote temperature sensors present | Yes/No/Unknown | Yes; No; Unknown | Conditional | Thermostat controls remote sensors | Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F145 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Remote sensor operation | Dropdown | Good; Failed; Out of calibration; N/A | Conditional | Remote sensors present | CLS / Under Armour, Rack Room Shoes | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F146 | 5 - Tech Entry Asset Basics | Electrical, Thermostat & Controls | EMS / BAS / DDC present | Yes/No/Unknown | Yes; No; Unknown | Recommended | Each controlled unit | Laser Facility / Kelly Services, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F147 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | EMS / BAS status and alarms | Text/Dropdown | Normal; Alarm; Offline; Communication fault; N/A | Conditional | EMS/BAS present | Laser Facility / Kelly Services, Vixxo / PepsiCo | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F148 | 5 - Tech Entry Asset Basics | Electrical, Thermostat & Controls | Economizer / outside-air damper present | Yes/No/Unknown | Yes; No; Unknown | Always | Airside unit | Broadway National / Primark, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F149 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Economizer / damper operation | Dropdown | Good; Stuck open; Stuck closed; Binding; Control fault; Adjusted; N/A | Conditional | Economizer/damper present | Broadway National / Primark, Rack Room Shoes, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F150 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Outdoor-air damper minimum position | Number/Text | Percent or measured position | Recommended | Economizer/damper present | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F151 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Outdoor-air screen / intake condition | Dropdown | Clean; Dirty; Damaged; Blocked; Missing; N/A | Conditional | Outdoor-air intake present | BOSS Facility Services, Powerhouse / Hibbett Sports | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F152 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Outdoor / fresh-air filter condition | Dropdown | Clean; Dirty; Replaced; N/A | Conditional | Fresh-air filter present | Broadway National / Primark | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F153 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Controls start-run-stop sequence | Dropdown | Pass; Fail; Intermittent; N/A | Always | Unit can operate | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F154 | 6 - Tech Entry Unit Specifics | Electrical, Thermostat & Controls | Active fault / diagnostic codes | Text | Code and description | Conditional | Electronic controls report codes | Industry best-practice addition | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F155 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Gas inlet pressure | Number | in. w.c. | Conditional | Gas heat | Victoria's Secret & Co. | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F156 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Gas manifold pressure | Number | in. w.c. | Conditional | Gas heat | CLS / Under Armour, Rack Room Shoes | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F157 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Gas leak detected | Yes/No | Yes; No | Conditional | Gas heat | CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F158 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Heat exchanger condition | Dropdown | Good; Rusted; Cracked; Hole; Failed; Unable to inspect, NA | Conditional | Fuel-fired heat | BOSS Facility Services, Broadway National / Primark, CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F159 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Burner condition | Dropdown | Clean; Dirty; Rusted; Damaged; Adjusted; N/A | Conditional | Fuel-fired heat | BOSS Facility Services, Laser Facility / Kelly Services, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F160 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Ignition / pilot operation | Dropdown | Pass; Fail; Intermittent; Cleaned; N/A | Conditional | Fuel-fired heat | BOSS Facility Services, Laser Facility / Kelly Services, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F161 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Combustion / draft inducer motor condition | Dropdown | Good; Noisy; Dirty; Failed; N/A | Conditional | Induced-draft heat | Broadway National / Primark, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F162 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Flue / vent condition | Dropdown | Good; Blocked; Corroded; Disconnected; Leaking; N/A | Conditional | Fuel-fired heat | Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F163 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Air pressure switch / end switch operation | Dropdown | Pass; Fail; N/A | Conditional | Applicable heating equipment | Broadway National / Primark | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F164 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Flame sensor signal | Number/Text | µA or Pass/Fail | Recommended | Fuel-fired heat | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F165 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Combustion CO reading | Number | ppm | Recommended | Fuel-fired heat and instrument available | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F166 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Flue temperature / combustion efficiency | Number | °F / % | Optional | Combustion analysis performed | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F167 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Electric heating coil condition | Dropdown | Good; Dirty; Damaged; Open element; N/A | Conditional | Electric heat | BOSS Facility Services, Victoria's Secret & Co. | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F168 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Electric heat stages operating | Repeating yes/no | Stage 1..n | Conditional | Electric heat | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F169 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | High-limit / safety control operation | Dropdown | Pass; Fail; N/A | Always | Heating equipment | Broadway National / Primark, BOSS Facility Services, Victoria's Secret & Co. | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F170 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Reversing valve operation | Dropdown | Pass; Fail; Sticking; N/A | Conditional | Heat pump | Laser Facility / Kelly Services | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F171 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Defrost controls / cycle | Dropdown | Pass; Fail; Unable to test; N/A | Conditional | Heat pump | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F172 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Auxiliary / emergency heat operation | Dropdown | Pass; Fail; N/A | Conditional | Heat pump with auxiliary heat | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F173 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Hot-water valve operation | Dropdown | Pass; Fail; Leaking; N/A | Conditional | Hot-water heat | Broadway National / Primark | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F174 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Entering water temperature | Number | °F | Conditional | Hydronic/water-cooled equipment | Broadway National / Primark | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F175 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Leaving water temperature | Number | °F | Conditional | Hydronic/water-cooled equipment | Broadway National / Primark | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F176 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Water pressure drop / flow | Number/Text | psi / gpm | Recommended | Hydronic/water-cooled equipment | Industry best-practice addition | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F177 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Water regulating valve condition | Dropdown | Good; Sticking; Leaking; Failed; N/A | Conditional | Water-cooled condenser | Broadway National / Primark | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F178 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Strainer condition / cleaned | Dropdown | Clean; Dirty; Cleaned; Damaged; N/A | Conditional | Hydronic/water-cooled equipment | BOSS Facility Services, Broadway National / Primark | Y | 0.016667 | Service Checklist items
HVAC PM Checklist | F179 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Glycol concentration / freeze protection | Number/Text | % and freeze point | Conditional | Glycol system | Broadway National / Primark | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F180 | 6 - Tech Entry Unit Specifics | Heating & Hydronic Readings | Frost stat / freeze stat operation | Dropdown | Pass; Fail; N/A | Conditional | Applicable system | Victoria's Secret & Co. | N | 0.016667 | Service Checklist items
HVAC PM Checklist | F181 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Deficiency ID | Auto-number | Sequential | Conditional | Issue found | Industry best-practice addition | N | 0.016667 | May not need this… IMO this would just be the quote WO#
HVAC PM Checklist | F182 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Related unit / component | Dropdown/Text | Unit and component | Conditional | Issue found | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | In checklist, then into quote workflow
HVAC PM Checklist | F183 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Deficiency description | Long text | What is wrong and evidence | Conditional | Issue found | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Y | 0.016667 | In checklist, then into quote workflow
HVAC PM Checklist | F184 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Condition severity | Dropdown | Observation; Needs Service; Urgent; Safety/Critical; Failed | Conditional | Issue found | Industry best-practice addition | N | 0.016667 | In checklist, then into quote workflow
HVAC PM Checklist | F185 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Current operational impact | Dropdown | None; Reduced capacity; Comfort issue; Water leak risk; Energy waste; Unit down; Safety hazard | Conditional | Issue found | Industry best-practice addition | N | 0.016667 | In checklist, then into quote workflow
HVAC PM Checklist | F186 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Expected risk before next PM | Dropdown | Low; Moderate; High; Imminent | Recommended | Issue found | Industry best-practice addition | N | 0.016667 | In checklist, then into quote workflow
HVAC PM Checklist | F187 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Recommended action | Dropdown/Text | Monitor; Clean; Adjust; Repair; Replace component; Replace unit; Further diagnosis | Conditional | Issue found | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | In checklist, then into quote workflow
HVAC PM Checklist | F188 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Parts / materials needed | Long text | Part numbers, sizes, quantities | Conditional | Repair recommended | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F189 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Estimated labor / access equipment | Text | Hours, technicians, lift/ladder | Recommended | Quote requested | Industry best-practice addition | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F190 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Quote / NTE required | Yes/No | Yes; No | Conditional | Issue found | Laser Facility / Kelly Services, CLS Equipment Condition Report, Off Broadway Shoe Warehouse, Rack Room Shoes | N | 0.016667 | Part of process…
HVAC PM Checklist | F191 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Call center contacted for NTE / quote | Yes/No/NA | Yes; No; N/A | Conditional | Immediate approval needed | Laser Facility / Kelly Services | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F192 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Quote / reference number | Text | Reference ID | Conditional | Quote created | Industry best-practice addition | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F193 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Material used - type | Dropdown/Text | Filter; Belt; Refrigerant; Battery; Fuse; Anti-algae tablet; Other | Conditional | Material used | Broadway National / Primark, Off Broadway Shoe Warehouse, Rack Room Shoes | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F194 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Material used - size / part number | Text | Size or part number | Conditional | Material used | Broadway National / Primark | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F195 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | Material used - quantity | Number | Quantity | Conditional | Material used | Broadway National / Primark | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F196 | 6 - Tech Entry Unit Specifics | Recommendations / Quote Readiness | General recommendations / comments | Long text | Free text | Always | Each unit / visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | In quote workflow….
HVAC PM Checklist | F197 | 7 - Tech Entry Check Out | Completion & Signoff | All panels reinstalled and secured | Yes/No/NA | Yes; No; N/A | Always | Every unit | Powerhouse / Hibbett Sports, Industry best-practice addition | Y | 0.016667 | Check out checklist
HVAC PM Checklist | F198 | 7 - Tech Entry Check Out | Completion & Signoff | Disconnects / power restored | Yes/No/NA | Yes; No; N/A | Always | Every unit | Industry best-practice addition | Y | 0.016667 | Check out checklist
HVAC PM Checklist | F199 | 7 - Tech Entry Check Out | Completion & Signoff | Work area and roof cleaned | Yes/No | Yes; No | Always | Every visit | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | Y | 0.016667 | Check out checklist
HVAC PM Checklist | F200 | 7 - Tech Entry Check Out | Completion & Signoff | Manager informed PM is complete | Yes/No/NA | Yes; No; N/A | Always | Occupied site | Laser Facility / Kelly Services | N | 0.016667 | Check out checklist
HVAC PM Checklist | F201 | 7 - Tech Entry Check Out | Completion & Signoff | Manager / customer printed name | Text | Free text | Conditional | Customer signoff required | BOSS Facility Services, Laser Facility / Kelly Services | N | 0.016667 | Check out checklist
HVAC PM Checklist | F202 | 7 - Tech Entry Check Out | Completion & Signoff | Manager / customer signature | Signature | Digital signature | Conditional | Customer signoff required | BOSS Facility Services | N | 0.016667 | Check out checklist
HVAC PM Checklist | F203 | 7 - Tech Entry Check Out | Completion & Signoff | Site stamp or customer initials | Image/Signature | Stamp image or initials | Conditional | Customer requires | BOSS Facility Services | N | 0.016667 | Check out checklist
HVAC PM Checklist | F204 | 7 - Tech Entry Check Out | Completion & Signoff | Technician signature | Signature | Digital signature | Always | Every visit | Victoria's Secret & Co. | N | 0.016667 | Check out checklist
HVAC PM Checklist | F205 | 1 - Already Built Into EvoTrakker | Completion & Signoff | Closeout date / time | Date-Time | Timestamp | Always | Every visit | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | N | 0.016667 | Check out checklist
HVAC PM Checklist | F206 | ???? | Completion & Signoff | Photo count uploaded | Number | Whole number | Always | Every visit | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | N | 0.016667 | Need more info on this… if needed, system could "count' photos added to ticket.
HVAC PM Checklist | F207 | ???? | Completion & Signoff | Invoice attached | Yes/No/NA | Yes; No; N/A | Conditional | Submission package built in same workflow | Laser Facility / Kelly Services, Broadway National / Primark | N | 0.016667 | OFFICE
HVAC PM Checklist | F208 | ???? | Completion & Signoff | Signoff attached | Yes/No/NA | Yes; No; N/A | Conditional | Customer requires | Laser Facility / Kelly Services | N | 0.016667 | OFFICE
HVAC PM Checklist | F209 | ???? | Completion & Signoff | Completed checklist attached | Yes/No | Yes; No | Always | Every visit | Laser Facility / Kelly Services, Broadway National / Primark, CLS / Under Armour | N | 0.016667 | OFFICE
HVAC PM Checklist | F210 | ???? | Completion & Signoff | Photos attached | Yes/No | Yes; No | Always | Every visit | Laser Facility / Kelly Services, Broadway National / Primark, CLS / Under Armour | N | 0.016667 | OFFICE
HVAC PM Checklist | F211 | 2 - PM Rules by Parent Trade | Completion & Signoff | Submission destination | Text | Portal/email/call center | Configured | Customer-specific | Laser Facility / Kelly Services | N | 0.016667 | OFFICE
HVAC PM Checklist | F212 | 1 - Already Built Into EvoTrakker | Completion & Signoff | Submission date / confirmation | Date-Time/Text | Timestamp/reference | Conditional | Package submitted | Broadway National / Primark | N | 0.016667 | OFFICE

## PM Tasks
Universal HVAC Preventive Maintenance Tasks and Readings
Task ID | Equipment Area | Task / Inspection | Standard Response | Reading / Data | Applies When | Requirement | Photo | Source Coverage | Notes
T001 | Arrival / Site | Take a clear photo of the front of the building | Completed / N/A |  | Every visit when required by customer | Customer-configured | Required | Laser Facility / Kelly Services
T002 | Arrival / Site | Check in with site manager and explain that HVAC PM is being performed | Completed / Not available |  | Occupied site | Always | No | Laser Facility / Kelly Services
T003 | Arrival / Site | Confirm special access needs and safely access every unit | Pass / Issue |  | Every visit | Always | Issue only | Laser Facility / Kelly Services
T004 | Cabinet / Exterior | Perform overall visual inspection of unit and service area | Pass / Needs Service / Failed / N/A |  | Every unit | Always | Required | Laser Facility / Kelly Services, BOSS Facility Services
T005 | Cabinet / Exterior | Inspect cabinet, paint, corrosion and physical damage | Condition status |  | Every unit | Always | Issue only | BOSS Facility Services, Powerhouse / Hibbett Sports
T006 | Cabinet / Exterior | Inspect for water or air leakage | Pass / Leak found / N/A |  | Every unit | Always | If issue | Powerhouse / Hibbett Sports
T007 | Cabinet / Exterior | Verify all panels, hinges and screws are present, secure and serviceable | Pass / Corrected / Needs repair |  | Every unit | Always | If issue | Powerhouse / Hibbett Sports, Laser Facility / Kelly Services
T008 | Cabinet / Exterior | Inspect internal insulation and panel condition | Condition status |  | Every unit | Always | If issue | BOSS Facility Services, Powerhouse / Hibbett Sports
T009 | Roof / Service Area | Inspect curb, stands, roof penetrations and service clearance | Pass / Needs Service / N/A |  | Rooftop or exterior units | Conditional | If issue | BOSS Facility Services, Powerhouse / Hibbett Sports
T010 | Roof / Service Area | Inspect piping and insulation for damage, rubbing, leaks or UV deterioration | Condition status |  | Applicable units | Always | If issue | BOSS Facility Services, Powerhouse / Hibbett Sports, Victoria's Secret & Co.
T011 | Roof / Service Area | Remove debris/trash and clean up around unit | Completed / Unable |  | Every unit | Always | After photo when required | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports
T012 | Filters | Inspect filter condition, fit, rack, seals and airflow direction | Pass / Needs Service / Failed / N/A |  | Filtered equipment | Always | Before photo | Industry best-practice addition
T013 | Filters | Replace all filters when included in scope | Completed / Not in scope / Unable | Sizes and quantities | Filtered equipment | Customer-configured | Before and after | Broadway National / Primark, CLS / Under Armour, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Rack Room Shoes
T014 | Filters | Write service date on replacement filters | Completed / N/A | Date | Filters replaced | Customer-configured | After photo | CLS / Under Armour, Laser Facility / Kelly Services, Powerhouse / Hibbett Sports
T015 | Filters | Show old filters to store staff before disposal | Completed / N/A | Manager name | Customer requires | Customer-configured | Optional | Rack Room Shoes
T016 | Fresh Air | Inspect and clean/replace fresh-air filters | Pass / Cleaned / Replaced / N/A |  | Fresh-air filters present | Conditional | If issue | Broadway National / Primark
T017 | Fans / Motors | Verify operation of supply, return, exhaust and booster fans | Pass / Fail / N/A | Amps / RPM if recorded | Applicable fans | Always | If issue | Laser Facility / Kelly Services
T018 | Fans / Motors | Inspect and clean blower wheels/fan blades | Clean / Cleaned / Damaged / N/A |  | Fan-equipped unit | Always | Before/after if dirty | Rack Room Shoes, Vixxo / PepsiCo
T019 | Fans / Motors | Inspect fan and motor mounting hardware; tighten as required | Pass / Tightened / Needs repair |  | Fan-equipped unit | Always | If issue | Victoria's Secret & Co., Powerhouse / Hibbett Sports
T020 | Fans / Motors | Inspect bearings for wear/noise/play and lubricate where required | Pass / Lubricated / Needs repair / N/A |  | Serviceable bearings | Always | If issue | Broadway National / Primark, Laser Facility / Kelly Services, Rack Room Shoes
T021 | Belts / Pulleys | Inspect belts for wear, cracks, glazing, contamination and correct tension | Pass / Adjusted / Quote replacement / Failed / N/A | Belt size/quantity | Belt-driven equipment | Conditional | Required | CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes
T022 | Belts / Pulleys | Inspect pulley/sheave condition and alignment | Pass / Adjusted / Needs replacement / N/A |  | Belt-driven equipment | Conditional | Required | CLS / Under Armour, Rack Room Shoes, Vixxo / PepsiCo
T023 | Belts / Pulleys | Verify shafts are aligned and components rotate freely | Pass / Fail / N/A |  | Belt-driven equipment | Conditional | If issue | Rack Room Shoes
T024 | Coils | Inspect condenser coil for dirt, damage and fin condition | Condition status |  | Cooling equipment | Always | Required | BOSS Facility Services, CLS / Under Armour, Rack Room Shoes, Victoria's Secret & Co.
T025 | Coils | Inspect evaporator coil for dirt, damage and fin condition | Condition status |  | Cooling equipment | Always | Required | BOSS Facility Services, CLS / Under Armour, Rack Room Shoes, Victoria's Secret & Co.
T026 | Coils | Brush/vacuum/wash coils as scope and access permit | Completed / Not needed / Deep clean quote / Unable |  | Dirty coils | Always | Before/after | Broadway National / Primark, Laser Facility / Kelly Services, Rack Room Shoes
T027 | Coils | Determine whether evaporator or condenser coils require a deep cleaning | Yes / No / N/A |  | Cooling equipment | Always | Required if Yes | Laser Facility / Kelly Services
T028 | Heating Coil | Inspect and clean heating coil or heat exchanger surfaces | Pass / Cleaned / Needs repair / N/A |  | Heating equipment | Conditional | Required | Rack Room Shoes, Victoria's Secret & Co.
T029 | Condensate | Inspect drain pan for rust, cracks, standing water, biological growth and overflow risk | Pass / Cleaned / Needs repair / N/A |  | Condensing equipment | Always | Required | BOSS Facility Services, Powerhouse / Hibbett Sports
T030 | Condensate | Clean/flush drain pan, drain line, trap, strainer and valves | Completed / Not needed / Unable / N/A |  | Condensing equipment | Always | Before/after | Broadway National / Primark, CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes
T031 | Condensate | Verify condensate drains freely and there are no leaks | Pass / Fail / N/A |  | Condensing equipment | Always | If issue | Industry best-practice addition
T032 | Condensate | Test overflow switch / float switch / condensate pump | Pass / Fail / N/A |  | Component present | Recommended | If issue | Industry best-practice addition
T033 | Condensate | Add anti-algae treatment to drain pan | Completed / N/A / Unable | Quantity/type | Customer requires | Customer-configured | Required | Off Broadway Shoe Warehouse, Rack Room Shoes
T034 | Electrical | Inspect disconnect, fuses, breakers, control panel and wiring | Pass / Needs Service / Failed / N/A | Voltage if taken | Every powered unit | Always | Required | BOSS Facility Services, Laser Facility / Kelly Services, Powerhouse / Hibbett Sports
T035 | Electrical | Check and tighten electrical connections where safe and permitted | Pass / Tightened / Needs repair |  | Every powered unit | Always | Interior photo | Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Rack Room Shoes
T036 | Electrical | Inspect for overheating, discoloration, corrosion, damaged insulation and loose terminals | Pass / Issue found |  | Every powered unit | Always | If issue | Industry best-practice addition
T037 | Electrical | Inspect starters, contactors, relays, solenoids and run capacitors | Pass / Needs Service / Failed / N/A | Capacitor µF if taken | Components present | Always | If issue | Broadway National / Primark, CLS / Under Armour, Vixxo / PepsiCo
T038 | Electrical | Test operating controls and safety controls | Pass / Fail / N/A |  | Every unit | Always | If issue | BOSS Facility Services, Broadway National / Primark, Rack Room Shoes, Victoria's Secret & Co.
T039 | Electrical | Measure motor voltage and current draw; compare with nameplate ratings | Pass / Out of range / Unable | Volts and amps | Operating motors | Recommended | Instrument display optional | Broadway National / Primark, CLS / Under Armour, BOSS Facility Services, Vixxo / PepsiCo
T040 | Electrical | Verify proper start, run and shutdown sequence | Pass / Fail / Intermittent |  | Unit can operate | Always | If issue | Industry best-practice addition
T041 | Thermostat / Controls | Verify thermostat operates the unit in cooling and heating modes | Pass / Fail / Unable / N/A | Setpoints | Thermostat-controlled equipment | Always | Required when customer requests | CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes
T042 | Thermostat / Controls | Verify remote sensors are present, communicating and reasonably calibrated | Pass / Fail / N/A | Sensor temperatures | Remote sensors present | Conditional | If issue | CLS / Under Armour, Rack Room Shoes
T043 | Thermostat / Controls | Record thermostat setpoints and schedule before making changes | Completed / N/A | Cooling, heating, schedule | Customer setpoint rules | Customer-configured | Required | Off Broadway Shoe Warehouse, Rack Room Shoes
T044 | Thermostat / Controls | Adjust thermostat to customer-required cooling/heating setpoints and schedule | Completed / Already correct / Unable | Final setpoints | Customer setpoint rules | Customer-configured | Required | Off Broadway Shoe Warehouse, Rack Room Shoes
T045 | Thermostat / Controls | Lock thermostat and verify programming/differential where required | Completed / N/A / Unable | Lock and differential | Customer rule requires | Customer-configured | Required | Off Broadway Shoe Warehouse, Rack Room Shoes, Laser Facility / Kelly Services
T046 | Thermostat / Controls | Replace thermostat batteries if needed | Completed / Not needed / N/A |  | Battery thermostat | Conditional | Optional | Laser Facility / Kelly Services
T047 | EMS / DDC | Verify DDC/EMS/BAS communication, schedules, commands and active alarms | Pass / Alarm / Offline / N/A | Alarm codes | DDC/EMS present | Conditional | Required | Laser Facility / Kelly Services, Vixxo / PepsiCo
T048 | Economizer | Verify economizer/outdoor-air damper operation and free movement | Pass / Adjusted / Fail / N/A | Damper position | Economizer present | Conditional | Required | Broadway National / Primark, Rack Room Shoes, Victoria's Secret & Co.
T049 | Economizer | Inspect damper motor, linkage, outside-air screen and intake | Pass / Cleaned / Needs repair / N/A |  | Outdoor-air system present | Conditional | If issue | Broadway National / Primark, BOSS Facility Services, Powerhouse / Hibbett Sports
T050 | Refrigeration | Inspect compressor and refrigerant lines for damage, vibration, oil traces and leaks | Pass / Issue found / N/A |  | Refrigeration equipment | Always | Required | Victoria's Secret & Co., Rack Room Shoes
T051 | Refrigeration | Inspect refrigerant valve packings and Schrader valves for leaks | Pass / Corrected / Leak found / N/A |  | Service valves/ports present | Conditional | If issue | Broadway National / Primark
T052 | Refrigeration | Install or tighten service-port caps | Completed / N/A |  | Service ports present | Conditional | Optional | Broadway National / Primark
T053 | Refrigeration | Inspect filter-drier, sight glass/moisture indicator and metering device operation | Pass / Needs Service / Failed / N/A |  | Components present | Always | If issue | Broadway National / Primark
T054 | Refrigeration | Verify refrigerant charge using appropriate readings | Proper / Low / High / Unable / N/A | Pressures, line temps, superheat, subcooling | Cooling system can operate | Always | Instrument displays recommended | Broadway National / Primark, Laser Facility / Kelly Services, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo
T055 | Refrigeration | Record ambient temperature and suction/discharge pressure for each circuit | Completed / Unable / N/A | Ambient, suction, discharge | Cooling system operating | Always | Optional | BOSS Facility Services, CLS / Under Armour, Victoria's Secret & Co.
T056 | Refrigeration | Record line temperatures, superheat and subcooling where applicable | Completed / Unable / N/A | Temperatures and calculated values | Cooling system operating | Recommended | Optional | Victoria's Secret & Co., Vixxo / PepsiCo
T057 | Compressor | Verify compressor operation, noise, vibration, oil level and amp draw | Pass / Needs Service / Failed / N/A | Oil level and amps | Compressor present | Always | If issue | BOSS Facility Services, Rack Room Shoes, Vixxo / PepsiCo
T058 | Compressor | Verify crankcase heater operation | Pass / Fail / N/A |  | Crankcase heater present / fall scope | Conditional | If issue | Broadway National / Primark, Laser Facility / Kelly Services
T059 | Condenser Fans | Manually verify condenser fan free movement with power safely isolated | Pass / Binding / N/A |  | Condenser fans present | Conditional | If issue | Victoria's Secret & Co.
T060 | Condenser Fans | Verify condenser fan operation, blade condition, bearings, mounting and amps | Pass / Needs Service / Failed / N/A | Amps | Condenser fans present | Always | If issue | BOSS Facility Services, Victoria's Secret & Co., Vixxo / PepsiCo
T061 | Heat Pump | Verify reversing valve and defrost operation | Pass / Fail / Unable / N/A |  | Heat pump | Conditional | If issue | Laser Facility / Kelly Services, Industry best-practice addition
T062 | Gas Heating | Inspect gas lines, valves and connections; check for leaks | Pass / Leak found / N/A | Gas pressure | Gas heat | Always | Required | CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes
T063 | Gas Heating | Inspect and clean burner assembly and combustion blower housing | Pass / Cleaned / Needs repair / N/A |  | Gas heat | Always | Before/after if dirty | Laser Facility / Kelly Services, Victoria's Secret & Co.
T064 | Gas Heating | Verify ignition/pilot, gas valve, end switch and pressure switch operation | Pass / Fail / N/A |  | Applicable gas heat | Always | If issue | Broadway National / Primark, Laser Facility / Kelly Services
T065 | Gas Heating | Inspect heat exchanger for cracks, holes, rust or damage | Pass / Failed / Unable to fully inspect / N/A |  | Fuel-fired heat | Always | Required | BOSS Facility Services, CLS / Under Armour, Laser Facility / Kelly Services, Rack Room Shoes, Victoria's Secret & Co.
T066 | Gas Heating | Inspect flue/vent system and verify safe draft | Pass / Needs Service / Failed / N/A | Draft/CO if measured | Fuel-fired heat | Always | If issue | Victoria's Secret & Co.
T067 | Gas Heating | Check gas inlet/manifold pressure | Pass / Out of range / Unable / N/A | in. w.c. | Gas heat operating | Conditional | Instrument display optional | CLS / Under Armour, Rack Room Shoes, Victoria's Secret & Co.
T068 | Gas Heating | Perform combustion safety check/analysis when required by scope or condition | Pass / Fail / N/A | CO, O2/CO2, flue temp, efficiency | Fuel-fired heat | Recommended | Instrument display | Industry best-practice addition
T069 | Electric Heating | Inspect and test electric heating elements, sequencers/contactors and limits | Pass / Needs Service / Failed / N/A | Stage amps | Electric heat | Always | If issue | BOSS Facility Services, Victoria's Secret & Co.
T070 | Hydronic Heating | Verify hot-water valve operation and inspect coil/piping | Pass / Leak / Failed / N/A | Entering/leaving water temp | Hot-water heat | Conditional | If issue | Broadway National / Primark
T071 | Hydronic / Water Cooled | Inspect water regulating valve, clean strainer and record entering/leaving water temperatures | Pass / Cleaned / Needs Service / N/A | Water temperatures | Water-cooled equipment | Conditional | If issue | Broadway National / Primark
T072 | Hydronic / Seasonal | Drain water coils or add/check glycol as required | Completed / N/A / Unable | Glycol % / freeze point | Seasonal water coil | Customer-configured | Optional | Broadway National / Primark
T073 | Heating Performance | Record return and supply temperatures and calculate temperature rise | Completed / Unable / N/A | Return, supply, rise | Heating mode can operate | Always | Optional | CLS / Under Armour
T074 | Air Distribution | Inspect supply and return grilles/diffusers for dirt, blockage and damage | Pass / Dirty / Blocked / Damaged / N/A |  | Ducted equipment | Always | Required if dirty | Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Rack Room Shoes, Vixxo / PepsiCo
T075 | Air Distribution | Clean grilles/diffusers when included in scope or prepare quote | Completed / Quote needed / Not needed / N/A |  | Dirty grilles found | Customer-configured | Before/after | Off Broadway Shoe Warehouse, Rack Room Shoes
T076 | Air Distribution | Check airflow and temperature at representative supply grilles | Pass / Weak airflow / Uneven / N/A | Temperature / velocity / CFM | Customer requests or comfort issue | Conditional | Instrument display optional | Off Broadway Shoe Warehouse
T077 | Air Distribution | Inspect accessible duct system for damage, disconnected sections, leakage and insulation defects | Pass / Issue found / N/A |  | Accessible duct system | Recommended | If issue | Vixxo / PepsiCo, Industry best-practice addition
T078 | Performance | Record supply, return, mixed-air and ambient temperatures as applicable | Completed / Unable / N/A | Temperatures | Unit can operate | Always | Optional | Broadway National / Primark, Rack Room Shoes, Vixxo / PepsiCo
T079 | Performance | Measure entering/leaving static pressure and calculate total external static | Completed / Unable / N/A | in. w.c. | Ducted equipment / scope requires | Recommended | Instrument display optional | Vixxo / PepsiCo
T080 | Closeout | Document all readings, work performed, materials, repairs and deficiencies | Completed |  | Every unit | Always | Issue photos | Laser Facility / Kelly Services
T081 | Closeout | Confirm all panels are secured, disconnects restored and unit left in safe operating condition | Pass / Shut down for safety / Unable |  | Every unit | Always | Required | Industry best-practice addition
T082 | Closeout | Inform site staff that PM is complete and capture manager name | Completed / No manager available / N/A | Manager name | Occupied site | Always | No | Laser Facility / Kelly Services
T083 | Closeout | Obtain customer signature/site stamp when required | Completed / Declined / N/A |  | Customer requires | Customer-configured | Required | BOSS Facility Services
T084 | Closeout | Complete IVR checkout / closeout | Completed / N/A / Failed | Confirmation number | Customer uses IVR | Customer-configured | No | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports
T085 | Closeout | Verify invoice, signoff, checklist, required photos and quotes are included in submission package | Complete / Missing items |  | Every visit | Always | No | Laser Facility / Kelly Services, Broadway National / Primark, CLS / Under Armour
T086 | Closeout | Report urgent issues and submit repair quote according to customer rules | Completed / N/A | Contact and quote reference | Urgent issue or quote required | Customer-configured | Issue photos | CLS Equipment Condition Report, CLS / Under Armour, Off Broadway Shoe Warehouse, Rack Room Shoes

## Photo Requirements
Master Photo Package
Photo ID | Photo / Evidence | Frequency | When Taken | Trigger | Time/Date Stamp | Source Coverage | Purpose / Notes
P01 | Front of building / storefront | Once per visit | Arrival | Customer requires | Customer-configured | Laser Facility / Kelly Services | Proves arrival at correct site.
P02 | Unit location / access path | Each unit | Before work | Always recommended | Optional | Laser Facility / Kelly Services | Shows rooftop/interior location and special access.
P03 | Unit overall exterior | Each unit | Before work | Always | Customer-configured | BOSS Facility Services, Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | Documents general condition.
P04 | Unit number / asset tag | Each unit | Before work | Always | Optional | Powerhouse / Hibbett Sports, Victoria's Secret & Co., Vixxo / PepsiCo | Ties all photos/readings to the correct asset.
P05 | Manufacturer nameplate | Each unit | Before work | Always | Optional | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Captures manufacturer, model, serial, electrical ratings, refrigerant and capacity.
P06 | Air-handler nameplate / connected asset | Each connected unit | Before work | Split/AHU systems | Optional | BOSS Facility Services, Vixxo / PepsiCo | Captures both halves of a split system.
P07 | Filters before replacement | Each filter bank | Before work | Filters replaced or condition issue | Customer-configured | CLS / Under Armour, Off Broadway Shoe Warehouse, Rack Room Shoes | Documents condition and quantity.
P08 | Filters after replacement and dated | Each filter bank | After work | Filters replaced | Customer-configured | CLS / Under Armour, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Rack Room Shoes | Verifies replacement, size, fit and date.
P09 | Unit interior / electrical compartment | Each unit | Before/after | Always or customer requires | Customer-configured | Off Broadway Shoe Warehouse, Rack Room Shoes, Laser Facility / Kelly Services | Documents cleanliness and electrical condition.
P10 | Condenser coil before/after | Each unit | Before and after cleaning | Dirty or cleaned | Customer-configured | Rack Room Shoes, Laser Facility / Kelly Services, Victoria's Secret & Co. | Shows coil condition and cleaning result.
P11 | Evaporator coil before/after | Each unit | Before and after cleaning | Accessible and dirty/cleaned | Customer-configured | Rack Room Shoes, Laser Facility / Kelly Services, Victoria's Secret & Co. | Shows coil condition and deep-clean need.
P12 | Drain pan / line / trap before and after | Each unit | Before/after cleaning | Condensate system present | Customer-configured | Off Broadway Shoe Warehouse, Rack Room Shoes | Verifies cleaning and drainage.
P13 | Anti-algae treatment in pan | Each pan | After work | Customer requires | Customer-configured | Off Broadway Shoe Warehouse, Rack Room Shoes | Verifies tablets/treatment were installed.
P14 | Belts / pulleys / sheaves | Each belt drive | Before/after adjustment | Belt-driven equipment | Optional | Powerhouse / Hibbett Sports, Rack Room Shoes | Documents size, condition, tension and alignment.
P15 | Blower wheel / fan / bearings | Each affected component | Before/after | Dirty, damaged or serviced | Optional | Rack Room Shoes, Vixxo / PepsiCo | Supports cleaning/repair recommendation.
P16 | Thermostat before changes | Each thermostat | Before work | Setpoint/schedule differs from customer rule | Required by some customers | Rack Room Shoes, Off Broadway Shoe Warehouse | Documents original cool/heat settings and schedule.
P17 | Thermostat after changes / locked | Each thermostat | After work | Customer setpoint rule applies | Required by some customers | Rack Room Shoes, Off Broadway Shoe Warehouse, Laser Facility / Kelly Services | Verifies final setpoints, differential and lock.
P18 | Remote sensor / controller / EMS screen | Each affected control | During test | Sensor/EMS issue or customer requires | Optional | Laser Facility / Kelly Services, Rack Room Shoes | Documents alarms, readings or communication status.
P19 | Supply and return grilles / diffusers | Representative areas | Before/after | Dirty, blocked, or customer requires | Customer-configured | Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Rack Room Shoes | Supports cleaning quote and airflow findings.
P20 | Refrigeration instrument readings | Each circuit | During operation | Pressure/temperature readings required | Optional | CLS / Under Armour, Victoria's Secret & Co., Vixxo / PepsiCo | Provides evidence of recorded readings.
P21 | Electrical meter / amp readings | Each abnormal reading | During operation | Reading out of range or customer requires | Optional | CLS / Under Armour, Vixxo / PepsiCo | Supports diagnosis and quote.
P22 | Heating section / burners / heat exchanger | Each heating unit | During inspection | Fuel-fired heat | Optional/issue required | CLS / Under Armour, Laser Facility / Kelly Services, Victoria's Secret & Co. | Documents safety condition.
P23 | Gas pressure / combustion readings | Each tested unit | During operation | Gas pressure or combustion test performed | Optional | CLS / Under Armour, Rack Room Shoes | Evidence of heating performance.
P24 | Roof/service area / curb / piping | Each issue | Before/after | Damage, debris, leak, insulation or access issue | Optional | BOSS Facility Services, Powerhouse / Hibbett Sports | Documents non-equipment conditions.
P25 | Every deficiency requiring repair or quote | At least one overview plus close-up | When found | Any deficiency | Customer-configured | BOSS Facility Services, Broadway National / Primark, CLS Equipment Condition Report, CLS / Under Armour, First Cash, Laser Facility / Kelly Services, Off Broadway Shoe Warehouse, Powerhouse / Hibbett Sports, Rack Room Shoes, Victoria's Secret & Co., Vixxo / PepsiCo | Mandatory evidence for quote-ready recommendations.
P26 | Unit after completion / panels secured | Each unit | After work | Recommended | Optional | Industry best-practice addition | Shows safe closeout.
P27 | Clean work area | Once per unit/area | After work | Customer requires or debris removed | Optional | Laser Facility / Kelly Services, Powerhouse / Hibbett Sports | Verifies housekeeping.
P28 | Customer signature / site stamp | Once per visit | Closeout | Customer requires | Optional | BOSS Facility Services | Supports invoice approval.

## Customer Exceptions
Customer-Specific Requirements and Conflicts
Customer / Source | Topic | Specific Requirement | Universal-Form Treatment
BOSS Facility Services | Equipment detail | Captures up to four units plus AHUs, filter and belt sizes/quantities, overall condition and area served. | Use repeatable unit and connected-AHU records.
BOSS Facility Services | Condition matrix | Rates cabinet, roof/service area, fan, electrical, condensing and heating components as Good/Fair/Poor. | Use the universal component status dropdown.
BOSS Facility Services | Readings/signoff | Ambient, multi-stage suction/discharge pressures, blower/condenser/compressor amps, customer signature and site stamp. | Make readings repeating by circuit and signoff conditional.
Broadway National / Primark | Detailed refrigeration | Valve packings, Schrader valves/caps, head/suction pressure, motor amps/volts, crankcase heaters, TXV and moisture indicator. | Show detailed refrigerant sub-section when applicable.
Broadway National / Primark | Water-cooled/seasonal | Water regulating valve, water temperatures, strainer, economizer, fresh-air filters, drain water coils and add glycol. | Use conditional water-cooled and seasonal tasks.
Broadway National / Primark | Submission | Checklist and photos must be submitted within one week for payment. | Store deadline in customer profile and require submission confirmation.
CLS Equipment Condition Report | Condition report | Operational good/poor, repairs needed/replacement, filter/belt data, full-scope completion and immediate quote requirement. | Use full-scope gate and deficiency record.
CLS / Under Armour | Required tasks/photos | Replace/date filters with photos; belts/pulleys; drains; coils; motor volts/amps; thermostat heat/cool; pressures; gas pressure; heat exchanger and gas leaks. | Map to core, cooling and heating sections.
First Cash | Asset inventory | System list includes submitter details, unit description, gas/electric, curb adapter and filter size. | Allow inventory-only mode and curb-adapter field.
Laser Facility / Kelly Services | Arrival and communication | Front-building photo, manager check-in, no pricing/details to store staff, unit location/access and shared-unit status. | Make communication rules customer-configured.
Laser Facility / Kelly Services | Controls and cleanup | DDC, crankcase heaters, ignition/burner, gas valve/leaks, VAV grilles, thermostat programming/batteries/differential, cleanup and manager name. | Use conditional control/heating tasks and closeout.
Off Broadway Shoe Warehouse | Photo rules | Time/date-stamped photos for filters, unit interior, drains and thermostat settings. | Customer profile controls timestamp and photo requirements.
Off Broadway Shoe Warehouse | Drain and thermostat | Add anti-algae tablets; thermostat target 70°F cooling and 68°F heating, locked full time. | Do not hard-code—load from profile.
Powerhouse / Hibbett Sports | Asset/condition detail | Cabinet, leakage, hinges, economizer, condensing, electrical, fan, heating, asset details, filter/belt, roof/service area and photos. | Universal component matrix plus expanded asset fields.
Rack Room Shoes | Filter and drain proof | Date-stamped filter photos, show old filters to staff, clean condensate system, add anti-algae and photograph. | Profile flags and photo checklist.
Rack Room Shoes | Thermostat conflict | Requires 71°F cooling and 68°F heating, 24/7 and locked. | This conflicts with Off Broadway's 70°F cooling requirement; use customer profile.
Rack Room Shoes | Detailed condition/readings | Coil, belt, pulley, shaft, bearing, supply temp/mode, refrigerant/oil leaks, gas pressure, compressor oil, economizer and remote sensors. | Use conditional detailed readings.
Victoria's Secret & Co. | Seasonal equipment types | Covers RTU, split, AHU, VAV, FPVAV and water-source heat pump with spring/fall sections. | Show tasks by equipment type and season.
Victoria's Secret & Co. | Cooling/heating readings | Ambient, suction/discharge by circuit, superheat, line temperatures, compressor/fan checks, flue, frost stat and safety switches. | Use repeating circuits and seasonal sections.
Vixxo / PepsiCo | Evaluation survey | Unit/AHU data, EER, life expectancy, repair/replace recommendation, component condition, FLA, pressures, superheat/subcooling, static pressure and EMS. | Use evaluation mode for condition surveys and quote planning.

## Dropdown Lists
Recommended Standardized Dropdown Values
List Name | Value | Meaning / Use
Task Result | Pass / Completed | Component/task is acceptable or work was completed.
Task Result | Needs Service | Unit operates but corrective service is recommended.
Task Result | Failed / Replace | Component failed or should be replaced.
Task Result | Not Applicable | Task/component does not apply to this unit.
Task Result | Not Accessible | Could not inspect because access was unavailable or unsafe.
Task Result | Unable to Test | Conditions did not permit a valid operational test.
Condition | Excellent | Like-new condition; no material defects.
Condition | Good | Normal wear; operating properly.
Condition | Fair | Noticeable wear; monitor or plan service.
Condition | Poor | Significant deterioration or unreliable operation.
Condition | Needs Replacement | Replacement recommended.
Overall Recommendation | None | No corrective action recommended.
Overall Recommendation | Monitor | Watch condition at future visits.
Overall Recommendation | Repair | Repair is recommended.
Overall Recommendation | Replace | Replacement is recommended.
Severity | Observation | Informational item only.
Severity | Needs Service | Non-urgent service recommended.
Severity | Urgent | Address promptly to avoid failure or damage.
Severity | Safety / Critical | Immediate safety or major operational risk.
Equipment Type | RTU | Packaged rooftop unit.
Equipment Type | Split System | Separate outdoor and indoor sections.
Equipment Type | AHU | Air handling unit.
Equipment Type | Heat Pump | Air-source heat pump.
Equipment Type | Water-Source Heat Pump | Water-loop heat pump.
Equipment Type | VAV | Variable air volume terminal/unit.
Equipment Type | FPVAV | Fan-powered VAV.
Equipment Type | Fan Coil | Fan-coil unit.
Equipment Type | VRF | Variable refrigerant flow system.
Equipment Type | Exhaust / Booster Fan | Standalone air-moving equipment.
Equipment Type | Refrigeration | Refrigeration equipment.
Equipment Type | Other | Describe in notes.
Heating Type | Gas | Natural gas or propane.
Heating Type | Electric | Electric resistance heat.
Heating Type | Heat Pump | Reverse-cycle heat.
Heating Type | Hot Water | Hydronic hot-water coil.
Heating Type | Steam | Steam coil.
Heating Type | None | Cooling/ventilation only.
PM Season | Spring Cooling | Cooling-season service.
PM Season | Fall Heating | Heating-season service.
PM Season | Full PM | Cooling and heating scope.
PM Season | Inspection Only | Condition survey without full maintenance.

## Reference Standards
Industry Reference Standards and Best-Practice Sources
Reference | Why It Matters | Official URL
ASHRAE Standard 180-2018 | Minimum inspection and maintenance requirements for commercial-building HVAC systems; intended to preserve thermal comfort, energy efficiency and indoor air quality. | https://www.ashrae.org/technical-resources/bookstore/standards-180-and-211
ASHRAE Titles, Purposes and Scopes | Official purpose and scope for ANSI/ASHRAE/ACCA Standard 180-2018. | https://www.ashrae.org/technical-resources/standards-and-guidelines/titles-purposes-and-scopes
DOE Better Buildings - Commercial HVAC Preventive Maintenance | Resources on commercial HVAC O&M, performance, equipment life and energy savings. | https://betterbuildingssolutioncenter.energy.gov/solutions-at-a-glance/preventative-maintenance-commercial-hvac-equipment
DOE - HVAC Commissioning | Highlights verification of HVAC performance, controls, economizers and demand-controlled ventilation. | https://www.energy.gov/cmei/buildings/hvac-commissioning
ENERGY STAR - O&M Best Practices | Emphasizes schedules, setpoints, controls, efficient operation and preventive maintenance. | https://www.energystar.gov/buildings/save-energy-commercial-buildings/ways-save/om-best-practices
ENERGY STAR - Maintenance Checklist | Includes drains, controls, coils, refrigerant, blower airflow and heating safety checks. | https://www.energystar.gov/saveathome/heating-cooling/maintenance-checklist
DOE FEMP - Equipment O&M Summaries | Federal O&M best-practice resources, including unitary HVAC equipment. | https://www.energy.gov/cmei/femp/equipment-operations-and-maintenance-summaries